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Supply Grilles & Registers



DAUSV
SINGLE DEFLECTION UNIVERSAL SPIRAL GRILLE

MODEL DESCRIPTION: Double deflection aluminum register with vertical front blades, horizontal rear blades, and opposed blade damper.
TYPE: Universal spiral grille. 
BLADE ARRANGEMENT: One one set of individually adjustable vertical blades spaced on 2/3 in. centers.
DAMPER: None; optional air scoop or tamper-resistant opposed blade damper.
FRAME: High-quality aluminum extruded frame for spiral/round duct applications.
FINISHES: W - White; M – Mill
PERFORMANCE BASIS: ANSI/ASHRAE Standard 70-2023
SUGGESTED SPECIFICATION
Furnish and install Dayus Model DAUSV Single Deflection Universal Spiral Grilles of the type, finish, listed size/opening size, and mounting method shown on the plans and air distribution schedules. The grilles shall be designed for installation on round or spiral duct without transition ductwork. The grilles shall have individually adjustable vertical blades spaced on 2/3 in. centers. Blades shall be roll-formed aluminum with semi-airfoil design and pressure-fit nylon pivot pins for rattle-free performance. The frame shall be high-quality extruded aluminum and supplied with a sealing gasket for a tight seal to the duct. Rear mullions shall be used for dimensions over 18 in. in length. Units shall be furnished in Dayus W White or M Mill finish as scheduled.
(Optional) Air scoop, tamper-resistant opposed blade damper, or No mounting configuration shall be provided where scheduled. Where double deflection is required, provide Dayus Model DAUSVH.
The manufacturer shall provide published performance data for the grille or register, which shall be tested in accordance with ANSI/ASHRAE Standard 70-2023.
STANDARD FEATURES
· Roll-formed aluminum blades with semi-airfoil design
· Pressure-fit nylon pivot pins for rattle-free performance
· Sealing gasket standard for tight seal to duct
· Available with durable powder coat finish
· Designed for round or spiral duct installation without transition ductwork; rear mullion used for dimensions over 18 in. in length.
RELATED OPTIONS / MODEL VARIANTS
· DAUSVD - Opposed blade damper
· DAUSV-AS - Air scoop
· DAUSVH - Double deflection
· DAUSV-TB - No mounting
Note: Use bracketed finish, size, mounting, and option selections from the project plans and air distribution schedule.
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